SELENIUM Headworks Analysis for T. Z. Osborne Local Limits Evaluation

Background Information

Selenium data from CY 2012 through CY 2014 will be used for this Selenium Headworks Analysis (HWA).  However, the average daily plant flow of 24.32 MGD for January 2014 through November 2014 will be used.

| TZ OSBORNE SELENIUM DATA | INFLUENT | EFFLUENT |
| --- | --- | --- |
| CY 2012 through CY 2014 |  |  |
| Number of Analyses | 48 | 48 |
| Number of Detections | 5/48 | 2/48 |
| Concentration Range: Minimum Value Maximum Value | <0.002 0.024 | <0.005 0.005 |

- The five influent values detected were as follows: 0.024 mg/l (6/25/2014); 0.01 mg/l (5/7/2014); 0.019 mg/l (4/30/2014); 0.011 mg/l (2/26/2014); and 0.013 mg/l (7/23/2013).

- The two effluent values detected were as follows: 0.005 mg/l (4/30/2014); and 0.004 mg/l (3/14/2012).

Removal Efficiency Calculations

Since more than 50% of the selenium data was Below Detection Limit (BDL), no removal efficiency calculations could be conducted using average daily removal efficiency [ADRE per July 2004 EPA LLG] or mean removal efficiency [MRE per July 2004 EPA LLG]. Based on the State of North Carolina PERCS Unit correspondence dated February 9, 2004 “the median literature value must be used if there is a higher percent of BDL or no site specific RR is determined.”

The selenium Literature Values for Activated Sludge Treatment from the July 2004 EPA Local Limits Guidance are as follows:

| Selenium Literature Values from 2004 EPA LLG | POTW Removal Efficiency |
| --- | --- |
| Median Value | 50% |

In reviewing the removal efficiencies using the various methods described above the City of Greensboro will use the Median Literature Value of 50% in this HWA.

Activated Sludge Inhibition Value

The July 2004 EPA LLG lists the selenium inhibition values as follows:

| Inhibition Values | mg/l [ppm] | ug/l [ppb] |
| --- | --- | --- |
| Activated Sludge | No EPA LLG Values |  |
| Nitrification | No EPA LLG Values |  |

There are no selenium inhibition literature values in the July 2004 EPA LLG document.

The City of Greensboro Industrial Waste Section conducted total selenium analyses on the activated sludge process at the T. Z. Osborne Water Reclamation Facility.  A summary of the quarterly aeration tank data from CY 2012 through CY 2014 is included with this submittal. The values ranged from <0.010 mg/l to 0.028 mg/l.  The maximum value of 0.028 mg/l was recorded on 12/11/2012 and will be used in the activated sludge/ nitrification Allowable Loading calculation.  A review of the T. Z. Osborne December 2012 DMR indicates the POTW was in full compliance.

Other Limiting Factors

North Carolina has established a Class C water quality standard of 0.005 mg/l for selenium.

The T. Z. Osborne NPDES permit NC0047384 issued July 1, 2014 includes the following new selenium limits.

| NPDES Limit | mg/l [ppm] |
| --- | --- |
| Monthly Average** (used in HWA) | 0.0052 |
| Daily Maximum | 0.0576 |

40 CFR Part 503 Sludge Criteria: Incineration [no HWA calculations conducted]

Although the City of Greensboro incinerates biosolids, land application (LA) metal parameters are analyzed as well and are more stringent for selenium.

- 40 CFR 503.13 LA Pollutant Concentration-Table 3 (“High Quality” Sludge Limits) = 100 mg/kg  (Greensboro is more than an order of magnitude lower than the LA regs)

- CY 2014 TZ Osborne Biosolids Average Selenium (11 samples) = 4.78 mg/kg

Allowable Influent Loadings Calculations

Activated Sludge:

0.028 mg/l x 8.34 x 24.32 MGD = 5.68 pounds

Nitrification:

0.028 mg/l x 8.34 x 24.32 MGD = 5.68 pounds

NPDES Permit Limit** Pass Through Calculation:

0.0052 mg/l/(1- 0.50) x 8.34 x 24.32 MGD = 2.11 pounds

MAHL Source:  NPDES Permit Limit Pass Through Calculation

MAHL for Selenium = 2.11 pounds